## Sheet1
Inputs for calculations |  |  |  |  | Normalized DATA Calculations
NPF - Normalized Permeate Flow - Calculations Inputs |  |  |  |  | NPF - Normalized Permeate Flow - Calculations Outputs
Parameter | Input Tag name | Baseline data |  | Current data | Parameter | Baseline data |  | Current data
Stage 1 - Feed conductivity | CIT-01 | µs | 3812 | 3812 | Stage 1 - cncentrate flow | m³h | 64 | 64
Stage 1 - Permeat flow | FIT-01 | m³h | 90 | 90 | Stage 1 - concentrate factor |  | 2.4062 | 2.4062
Stage 2 - Permeat flow | FIT-02 | m³h | 27 | 27 | Stage 2 - concentrate factor |  | 1.7297 | 1.7297
Cncentrate flow | FIT-03 | m³h | 37 | 37 | Stage 1 - feed TDS | mg/l | 2554.04 | 2554.04
Stage 1 - feed pressure | PIT-03 | bar | 10.2 | 10.5 | Stage 1 - concentrate TDS | mg/l | 6145.6587 | 6145.6587
Stage 1 - concentrate pressure | PIT-04 | bar | 9 | 9.15 | Stage 2 - concentrate TDS | mg/l | 10630.3286 | 10630.3286
Stage 2 - feed pressure | PIT-05 | bar | 9.5 | 9.5 | Stage 1 - aNDP |  | 79.7515 | 83.014
Stage 2 - concentrate pressure | PIT-06 | bar | 8.3 | 8.23 | Stage 2 - aNDP |  | 29.2201 | 28.7126
Permeate pressure | PIT-07 | bar | 1.1 | 1.1 | TCF |  | 0.85969 | 0.91385
Feed water temperature | TIT-01 | °C | 20 | 22 | Stage 1 - Baseline Net Permeate Flow | 90
[5 empty] | Stage 1 - Current Net Permeate Flow | 81.3393
[5 empty] | Stage 2 - Baseline Net Permeate Flow | 27
[5 empty] | Stage 2 - Current Net Permeate Flow | 25.849
NSR - Normalized Salt Rejection - Calculations Inputs |  |  |  |  | NSR - Normalized Rejection - Calculations Outputs
Parameter |  | Baseline data |  | Current data | Parameter | Baseline data |  | Current data
Permeate conductivity | CIT-01 | µs | 120 | 120 | Permeate TDS | mg/l | 80.4 | 80.4
[5 empty] | Salt Rejection |  | 0.96852 | 0.96852
[5 empty] | Salt passage |  | 0.03148 | 0.03148
[5 empty] | Normalized Salt Rejection | % | 97.2937 | 97.1233
NPD - Normalized Pressure Drop - Calculations Inputs
[5 empty] | Parameter | Baseline data |  | Current data
[5 empty] | Stage 1 - Pressure Drop | bar | 1.2 | 1.35
[5 empty] | Stage 1 -Average flow | m³h | 77 | 77
[5 empty] | Stage 2 - Pressure Drop | bar | 1.2 | 1.27
[5 empty] | Stage 2 -Average flow | m³h | 32 | 32
[5 empty] | Stage 1 - Normalized Pressure Drop | bar | 1.2 | 1.35
[5 empty] | Stage 2 - Normalized Pressure Drop | bar | 1.2 | 1.27